## CALCULATOR
[7 empty] | Panduit Patch Cord Approximate Diameters | [5 empty] | Cat 6A Plenum UTP Cable | Dia. (in.)
[13 empty] | Panduit Vari-MaTriX HD | 0.23
[7 empty] | Cat. | AWG | in. |  | mm |  | Panduit Std Comp+ HD | 0.23
[7 empty] | 5e | 28 | 0.149 |  | 3.7846 |  | CommScope 2091B | 0.285
[7 empty] | 5e | 24 | 0.215 |  | 5.461 |  | CommScope 2091SD | 0.265
[7 empty] | 6 | 28 | 0.15 |  | 3.81 |  | Belden 10GXS | 0.265
Enter the cable diameter below and select in. or mm. | [6 empty] | 6 | 24 | 0.235 |  | 5.969 |  | Berk-Tek LANmark-XTP | 0.275
[7 empty] | 6A | 28 | 0.185 |  | 4.699
Cable Diameter = | 0.185 | 1 |  |  |  |  | 6A | 24 | 0.25 |  | 6.35
| Duplex Cable? | 1
Product Family | Part Number | Description | Cable Manager Area |  |  | Recommended Cable Fill (30%) |  |  |  | Maximum Cable Fill (50%)
|  |  | Front Usable Area (sq. in.) | Rear Usable Area (sq. in.) | Total Usable Area (sq. in.) | Front | Rear | Total |  | Front | Rear | Total
PR2V PatchRunner™ 2 Vertical Cable Managers | PR2VD06 | 6" wide | 45.11 | 27.26 | 72.37 | 503 | 304 | 807 |  | 839 | 507 | 1346
| PR2VFD06 | 6" wide, front only | 45.11 | 0 | 45.11 | 503 | 0 | 503 |  | 839 | 0 | 839
| PR2VD08 | 8" wide | 63.71 | 39.73 | 103.44 | 711 | 443 | 1154 |  | 1185 | 739 | 1924
| PR2VFD08 | 8" wide, front only | 63.71 | 0 | 63.71 | 711 | 0 | 711 |  | 1185 | 0 | 1185
| PR2VD10 | 10" wide | 82.31 | 52.21 | 134.52 | 918 | 582 | 1501 |  | 1531 | 971 | 2502
| PR2VFD10 | 10" wide, front only | 82.31 | 0 | 82.31 | 918 | 0 | 918 |  | 1531 | 0 | 1531
| PR2VD12 | 12" wide | 100.9 | 64.68 | 165.58 | 1126 | 721 | 1847 |  | 1876 | 1203 | 3079
| PR2VFD12 | 12" wide, front only | 100.9 | 0 | 100.9 | 1126 | 0 | 1126 |  | 1876 | 0 | 1876
| Single PR2V Finger |  |  |  | 5.8 | 64 |  |  |  | 107
PR2VRG PatchRunner™2 Rear Gate Accessory | PR2VRGSK06 | 6" wide gate kit | 0 | 43.45 | 43.45 | 0 | 484 | 484 |  | 0 | 808 | 808
| PR2VRGSK08 | 8" wide gate kit | 0 | 59.51 | 59.51 | 0 | 664 | 664 |  | 0 | 1106 | 1106
| PR2VRGSK10 | 10" wide gate kit | 0 | 75.57 | 75.57 | 0 | 843 | 843 |  | 0 | 1405 | 1405
| PR2VRGSK12 | 12" wide gate kit | 0 | 91.63 | 91.63 | 0 | 1022 | 1022 |  | 0 | 1704 | 1704
PR2HF PatchRunner™2 Horizontal Cable Managers | PR2HF1 | 1RU, front only | 5.1 | 0 | 5.1 | 56 | 0 | 56 |  | 94 | 0 | 94
| PR2HF2 | 2RU, front only | 12.5639 | 0 | 12.5639 | 140 | 0 | 140 |  | 233 | 0 | 233
| PR2HF3 | 3RU, front only | 23.0956 | 0 | 23.0956 | 257 | 0 | 257 |  | 429 | 0 | 429
| PR2HF4 | 4RU, front only | 33.6272 | 0 | 33.6272 | 375 | 0 | 375 |  | 625 | 0 | 625
PE2V PatchRunner™ 2 High Capacity Vertical Cable Managers | PE2VD06 | 6" wide | 66.1018 | 44.2782 | 110.38 | 737 | 494 | 1231 |  | 1229 | 823 | 2053
| PE2VFD06 | 6" wide, front only | 66.1018 | 0 | 66.1018 | 737 | 0 | 737 |  | 1229 | 0 | 1229
| PE2VD08 | 8" wide | 92.4809 | 63.0973 | 155.5782 | 1032 | 704 | 1736 |  | 1720 | 1173 | 2893
| PE2VFD08 | 8" wide, front only | 92.4809 | 0 | 92.4809 | 1032 | 0 | 1032 |  | 1720 | 0 | 1720
| PE2VD10 | 10" wide | 118.8599 | 81.9639 | 200.8238 | 1326 | 914 | 2241 |  | 2210 | 1524 | 3735
| PE2VFD10 | 10" wide, front only | 118.8599 | 0 | 118.8599 | 1326 | 0 | 1326 |  | 2210 | 0 | 2210
| PE2VD12 | 12" wide | 145.239 | 100.7355 | 245.9745 | 1620 | 1124 | 2745 |  | 2701 | 1873 | 4575
| PE2VFD12 | 12" wide, front only | 145.239 | 0 | 145.239 | 1620 | 0 | 1620 |  | 2701 | 0 | 2701
| Single PE2V Finger |  |  |  | 5.8 | 64 |  |  |  | 107
WMPV NetRunner™ Vertical Cable Managers | WMPV22E | 4.9" wide, 22RU | 17.3 | 17.3 | 34.6 | 193 | 193 | 386 |  | 321 | 321 | 643
| WMPVF22E | 4.9" wide, 22RU, front only | 17.3 | 0 | 17.3 | 193 | 0 | 193 |  | 321 | 0 | 321
| WMPV45E | 4.9" wide, 45RU | 17.3 | 17.3 | 34.6 | 193 | 193 | 386 |  | 321 | 321 | 643
| WMPVF45E | 4.9" wide, 45RU, front only | 17.3 | 0 | 17.3 | 193 | 0 | 193 |  | 321 | 0 | 321
| WMPVHC45E | 6.7" wide, 45RU | 30.7 | 30.7 | 61.4 | 342 | 342 | 685 |  | 571 | 571 | 1142
| WMPVHCF45E | 6.7" wide, 45RU, front only | 30.7 | 0 | 30.7 | 342 | 0 | 342 |  | 571 | 0 | 571
| Single WMPV Finger |  |  |  | 3.7 | 41 |  |  |  | 68
| Single WMPVHC Finger |  |  |  | 4.7 | 52 |  |  |  | 87
WMP PatchLink™ Horizontal Cable Managers | WMP1E | 2RU, front/rear | 7.6 | 10.6 | 18.2 | 84 | 118 | 203 |  | 141 | 197 | 338
| WMPF1E | 2RU, front only | 7.6 | 0 | 7.6 | 84 | 0 | 84 |  | 141 | 0 | 141
| WMPH2E | 2RU, front/rear, w/ bend rad. clips | 5.9 | 10.6 | 16.5 | 65 | 118 | 184 |  | 109 | 197 | 306
| WMPHF2E | 2RU, front only, w/ bend rad. clips | 5.9 | 0 | 5.9 | 65 | 0 | 65 |  | 109 | 0 | 109
| WMPSE | 1RU, front/rear | 3.5 | 6.3 | 9.8 | 39 | 70 | 109 |  | 65 | 117 | 182
| WMPFSE | 1RU, front only | 3.5 | 0 | 3.5 | 39 | 0 | 39 |  | 65 | 0 | 65
| WMPLSE | 1RU, front/rear, short depth | 2.1 | 6.3 | 8.4 | 23 | 70 | 93 |  | 39 | 117 | 156
| WMPLFSE | 1RU, front only, short depth | 2.1 | 0 | 2.1 | 23 | 0 | 23 |  | 39 | 0 | 39
Note: Rear section may be partially blocked by rack posts
NCMH NetManager™ Horizontal Cable Managers | NCMH2 | 2RU, front/rear | 6 | 8 | 14 | 66 | 89 | 156 |  | 111 | 148 | 260
| NCMHF2 | 2RU, front only | 6 | 0 | 6 | 66 | 0 | 66 |  | 111 | 0 | 111
| NCMHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 25 | 0 | 25 |  | 42 | 0 | 42
NM NetManager™ High Capacity Horizontal Cable Managers | NM1 | 1RU, front/rear | 3.3 | 4.1 | 7.4 | 36 | 45 | 82 |  | 61 | 76 | 137
| NMF1 | 1RU, front only | 3.3 | 0 | 3.3 | 36 | 0 | 36 |  | 61 | 0 | 61
| NM2 | 2RU, front/rear | 9.8 | 11.1 | 20.9 | 109 | 123 | 233 |  | 182 | 206 | 388
| NMF2 | 2RU, front only | 9.8 | 0 | 9.8 | 109 | 0 | 109 |  | 182 | 0 | 182
| NM3 | 3RU, front/rear | 17.3 | 22 | 39.3 | 193 | 245 | 438 |  | 321 | 409 | 731
| NMF3 | 3RU, front only | 17.3 | 0 | 17.3 | 193 | 0 | 193 |  | 321 | 0 | 321
| NM4 | 4RU, front/rear | 24.3 | 31.9 | 56.2 | 271 | 356 | 627 |  | 452 | 593 | 1045
| NMF4 | 4RU, front only | 24.3 | 0 | 24.3 | 271 | 0 | 271 |  | 452 | 0 | 452
Note: Rear section may be partially blocked by rack posts
CMPH Open-Access™ Horizontal Cable Managers | CMPH1 | 1RU, front/rear | 2.3 | 2.9 | 5.2 | 25 | 32 | 58 |  | 42 | 53 | 96
| CMPHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 25 | 0 | 25 |  | 42 | 0 | 42
| CMPH2 | 2RU, front/rear | 5.3 | 10.8 | 16.1 | 59 | 120 | 179 |  | 98 | 200 | 299
| CMPHF2 | 2RU, front only | 5.3 | 0 | 5.3 | 59 | 0 | 59 |  | 98 | 0 | 98
| CMPHH2 | 2RU, front only, larger D-rings | 10.8 | 0 | 10.8 | 120 | 0 | 120 |  | 200 | 0 | 200
| CMPHHF1 | 1RU, front only, larger D-rings | 2.9 | 0 | 2.9 | 32 | 0 | 32 |  | 53 | 0 | 53
Note: Rear section may be partially blocked by rack posts
CMVDR Vertical D-rings | CMVDR1 | 5.70"L x 2.00"W |  |  | 6 |  |  | 66 |  |  |  | 111
| CMVDR1S | 3.30"L x 2.00"W |  |  | 3 |  |  | 33 |  |  |  | 55
| CMVDR2 | 5.70"L x 3.00"W |  |  | 10.8 |  |  | 120 |  |  |  | 200
| CMVDR2S | 3.30"L x 3.00"W |  |  | 6 |  |  | 66 |  |  |  | 111
| CMVDRC | between-racks, 5.60"L x 8.00"W |  |  | 24 |  |  | 267 |  |  |  | 446
CM Cable Routing Troughs | CMLT19 | lower trough w/ bend radius |  |  | 22.7 |  |  | 253 |  |  |  | 422
| CMUT19 | upper trough w/ bend radius |  |  | 8.2 |  |  | 91 |  |  |  | 152
| CMT4 | horizontal trough |  |  | 21.9 |  |  | 244 |  |  |  | 407
*Capacity is calculated for within the trough channel only. Higher capacities can be achieved when cables are tied together.
CWMPV IN-Cabinet Vertical Cable Manager | CWMPV2440 | side mount, 2"W x 4"D x 6'H | 5.7 | 0 | 5.7 | 63 | 0 | 63 |  | 106 | 0 | 106
| CWMPV3440 | side mount, 3"W x 4"D x 6'H | 9.1 | 0 | 9.1 | 101 | 0 | 101 |  | 169 | 0 | 169
| CWMPV2340 | side mount, 2"W x 3"D x 6'H | 5.2 | 0 | 5.2 | 58 | 0 | 58 |  | 96 | 0 | 96
| CWMPV3340 | side mount, 3"W x 3"D x 6'H | 7.8 | 0 | 7.8 | 87 | 0 | 87 |  | 145 | 0 | 145
4-Post Rack Vertical Tie-off Panels | V4PTOB | Vertical Tie-off Panel with AR4P 4-Post Racks | 31.7 | 0 | 31.7 | 353 | 0 | 353 |  | 589 | 0 | 589
| V4PTOB | Vertical Tie-off Panel with R4P 4-Post Racks | 35.8 | 0 | 35.8 | 399 | 0 | 399 |  | 665 | 0 | 665
| V4PATOB | Adjustable Depth Vertical Tie-off Panel with AR4P 4-Post Racks | 43.9 | 0 | 43.9 | 489 | 0 | 489 |  | 816 | 0 | 816
| V4PATOB | Adjustable Depth Vertical Tie-off Panel with R4P 4-Post Racks | 49.6 | 0 | 49.6 | 553 | 0 | 553 |  | 922 | 0 | 922
J-PRO & J-MOD J Hooks | JP75^ | J-Pro™ cable support, 0.75" |  |  | 0.626 |  |  | 9 |  |  |  | 9
| JP131^ | J-Pro™ cable support, 1.31" |  |  | 1.74 |  |  | 25 |  |  |  | 25
| JP2^ | J-Pro™ cable support, 2.0" |  |  | 3.155 |  |  | 46 |  |  |  | 46
| JP4^ | J-Pro™ cable support, 4.0" |  |  | 13.478 |  |  | 200 |  |  |  | 200
| JMJH2^ | J-Mod™ cable support, 2.0" |  |  | 3.037 |  |  | 45 |  |  |  | 45
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
EMT Electrical Metallic Tubing | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 4 |  |  |  | 4
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 7 |  |  |  | 7
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 12 |  |  |  | 12
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 22 |  |  |  | 22
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0367 |  |  | 30 |  |  |  | 30
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 49 |  |  |  | 49
| 2-1/2" | Useable Inside Diameter in inches | 2.731 |  | 5.8601 |  |  | 87 |  |  |  | 87
| 3" | Useable Inside Diameter in inches | 3.356 |  | 8.8493 |  |  | 131 |  |  |  | 131
| 3-1/2" | Useable Inside Diameter in inches | 3.834 |  | 11.5497 |  |  | 171 |  |  |  | 171
| 4" | Useable Inside Diameter in inches | 4.334 |  | 14.7585 |  |  | 219 |  |  |  | 219
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
EMT Electrical Metallic Tubing* | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 4 |  |  |  | 4
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 7 |  |  |  | 7
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 12 |  |  |  | 12
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 22 |  |  |  | 22
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0367 |  |  | 30 |  |  |  | 30
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 49 |  |  |  | 49
| 2-1/2" | Useable Inside Diameter in inches | 2.731 |  | 5.8601 |  |  | 87 |  |  |  | 87
| 3" | Useable Inside Diameter in inches | 3.356 |  | 8.8493 |  |  | 131 |  |  |  | 131
| 3-1/2" | Useable Inside Diameter in inches | 3.834 |  | 11.5497 |  |  | 171 |  |  |  | 171
| 4" | Useable Inside Diameter in inches | 4.334 |  | 14.7585 |  |  | 219 |  |  |  | 219
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
IMC Intermediate Conduit* | 1/2" | Useable Inside Diameter in inches | 0.675 |  | 0.35799 |  |  | 5 |  |  |  | 5
| 3/4" | Useable Inside Diameter in inches | 0.879 |  | 0.60708 |  |  | 9 |  |  |  | 9
| 1" | Useable Inside Diameter in inches | 1.12 |  | 0.9856 |  |  | 14 |  |  |  | 14
| 1-1/4" | Useable Inside Diameter in inches | 1.468 |  | 1.6932 |  |  | 25 |  |  |  | 25
| 1-1/2" | Useable Inside Diameter in inches | 1.703 |  | 2.2787 |  |  | 33 |  |  |  | 33
| 2" | Useable Inside Diameter in inches | 2.17 |  | 3.6998 |  |  | 55 |  |  |  | 55
| 2-1/2" | Useable Inside Diameter in inches | 2.597 |  | 5.2992 |  |  | 78 |  |  |  | 78
| 3" | Useable Inside Diameter in inches | 3.216 |  | 8.1264 |  |  | 120 |  |  |  | 120
| 3-1/2" | Useable Inside Diameter in inches | 3.711 |  | 10.8205 |  |  | 161 |  |  |  | 161
| 4" | Useable Inside Diameter in inches | 4.205 |  | 13.893 |  |  | 206 |  |  |  | 206
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
Rigid Conduit Steel or Aluminum* | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 4 |  |  |  | 4
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 7 |  |  |  | 7
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 12 |  |  |  | 12
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 22 |  |  |  | 22
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0367 |  |  | 30 |  |  |  | 30
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 49 |  |  |  | 49
| 2-1/2" | Useable Inside Diameter in inches | 2.469 |  | 4.7897 |  |  | 71 |  |  |  | 71
| 3" | Useable Inside Diameter in inches | 3.068 |  | 7.3956 |  |  | 110 |  |  |  | 110
| 3-1/2" | Useable Inside Diameter in inches | 3.548 |  | 9.8908 |  |  | 147 |  |  |  | 147
| 4" | Useable Inside Diameter in inches | 4.026 |  | 12.7354 |  |  | 189 |  |  |  | 189
| 5" | Useable Inside Diameter in inches | 5.047 |  | 20.0139 |  |  | 297 |  |  |  | 297
| 6" | Useable Inside Diameter in inches | 6.065 |  | 28.9019 |  |  | 430 |  |  |  | 430
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
Cable Capacity Calculator V13

## LEGACY
[7 empty] | Panduit Patch Cord Approximate Diameters | [5 empty] | Cat 6A Plenum UTP Cable | Dia. (in.)
[13 empty] | Panduit Vari-MaTriX HD | 0.23
[7 empty] | Cat. | AWG | in. |  | mm |  | Panduit Std Comp+ HD | 0.23
[7 empty] | 5e | 28 | 0.149 |  | 3.7846 |  | CommScope 2091B | 0.285
[7 empty] | 5e | 24 | 0.215 |  | 5.461 |  | CommScope 2091SD | 0.265
[7 empty] | 6 | 28 | 0.15 |  | 3.81 |  | Belden 10GXS | 0.265
Enter the cable diameter below and select in. or mm. | [6 empty] | 6 | 24 | 0.235 |  | 5.969 |  | Berk-Tek LANmark-XTP | 0.275
[7 empty] | 6A | 28 | 0.185 |  | 4.699
Cable Diameter = | 0.3 | 1 |  |  |  |  | 6A | 24 | 0.25 |  | 6.35
| Duplex Cable? | 1
Product Family | Part Number | Description | Cable Manager Area |  |  | Recommended Cable Fill (30%) |  |  |  | Maximum Cable Fill (50%)
|  |  | Front Usable Area (sq. in.) | Rear Usable Area (sq. in.) | Total Usable Area (sq. in.) | Front | Rear | Total |  | Front | Rear | Total
NRV NetRunner™ High Capacity Vertical Cable Managers | NRV10 | 10" wide, 45RU | 49.1 | 49.1 | 98.2 | 208 | 208 | 416 |  | 347 | 347 | 694
| NRVF10 | 10" wide, 45RU, front only | 49.1 | 0 | 49.1 | 208 | 0 | 208 |  | 347 | 0 | 347
| Single NRV Finger |  |  |  | 4.7 | 19 |  |  |  | 33
PEHF PatchRunner™ High Capacity Horizontal Cable Managers | PEHF2 | 2RU, front only | 16.6 | 0 | 16.6 | 70 | 0 | 70 |  | 117 | 0 | 117
| PEHF3 | 3RU, front only | 29.6 | 0 | 29.6 | 125 | 0 | 125 |  | 209 | 0 | 209
| PEHF4 | 4RU, front only | 42.8 | 0 | 42.8 | 181 | 0 | 181 |  | 302 | 0 | 302
CWMPV IN-Cabinet Vertical Cable Manager | CWMPV2418 | side mount, 2"W x 4"D x 2.6'H | 5.7 | 0 | 5.7 | 24 | 0 | 24 |  | 40 | 0 | 40
| CWMPV3418 | side mount, 3"W x 4"D x 2.6'H | 9.1 | 0 | 9.1 | 38 | 0 | 38 |  | 64 | 0 | 64
| CWMPV2318 | side mount, 2"W x 3"D x 2.6'H | 5.2 | 0 | 5.2 | 22 | 0 | 22 |  | 36 | 0 | 36
| CWMPV3318 | side mount, 3"W x 3"D x 2.6'H | 7.8 | 0 | 7.8 | 33 | 0 | 33 |  | 55 | 0 | 55
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
Cable Capacity Calculator V12

## numbers (hidden)
in. | no
mm | yes
30% | 40%
50% | 40%
0.215 | 0.185 | 0.275 | 0.15 | 0.235