## CALCULATOR
[6 empty] | Panduit Patch Cord Approximate Diameters |  |  |  |  | Cat 6A Plenum UTP Cable | Dia. (in.) | A/V Cable Approximate Diameters
[6 empty] | Cat. | AWG | in. |  | mm | Panduit Vari-MaTriX HD | 0.23 | TYPE | in. | mm
[6 empty] | 5e | 28 | 0.149 |  | 3.7846 | Panduit Std Comp+ HD | 0.23 | RG6 | 0.275 | 6.985
[6 empty] | 5e | 24 | 0.215 |  | 5.461 | CommScope 2091B | 0.285
[6 empty] | 6 | 28 | 0.15 |  | 3.81 | CommScope 2091SD | 0.265
Enter the cable diameter below and select in. or mm. | [5 empty] | 6 | 24 | 0.235 |  | 5.969 | Belden 10GXS | 0.265 | Fiber Optic Cable Approximate Diameters
[6 empty] | 6A | 28 | 0.185 |  | 4.699 | Berk-Tek LANmark-XTP | 0.275
Cable Diameter = | 0.25 | 1 |  |  |  | 6A | 24 | 0.25 |  | 6.35 |  |  | TYPE | in. | mm
| Duplex Cable? | 1 | [10 empty] | 2 Strand | 0.175 | 4.445
| Power Cable? | 1 | Power Cable AWG | 2
Product Family | Description |  | Total Usable Area (sq. in.) |  | Recommended Cable Fill (40%) |  |  |  | Maximum Cable Fill (60%)
[5 empty] | Total |  |  |  | Total
T-70 Raceway | T-70: No devices |  | 5.15 |  | 41 |  |  |  | 62
| T-70: Divided Power and Data Using the 3-sided Hanging Box and Device Bracket (POWER) |  | 0.86 |  | NA |  |  |  | NA
| T-70: Divided Power and Data Using the 3-sided Hanging Box and Device Bracket (DATA) |  | 1.72 |  | 14 |  |  |  | 21
| T-70: Data only using Screw- on Faceplates |  | 3.67 |  | 29 |  |  |  | 44
| T-70: Data only using Snap- on Faceplates |  | 4.71 |  | 38 |  |  |  | 57
| T-70: Divided Power and Data using the WORKSTATION OUTLET CENTER™ Offset Box (POWER) |  | 0.91 |  | NA |  |  |  | NA
| T-70: Divided Power and Data using the WORKSTATION OUTLET CENTER™ Offset Box (DATA) |  | 3.12 |  | 25 |  |  |  | 38
T-45 Raceway | T-45 : No devices |  | 2.13 |  | 17 |  |  |  | 26
| T-45: No devices with wire retainer |  | 1.72 |  | 14 |  |  |  | 21
| T-45: Divided Power and Data with wire retainer & divider wall (2 channels) (POWER) |  | 0.44 |  | NA |  |  |  | NA
| T-45: Divided Power and Data with wire retainer & divider wall (2 channels) (DATA) |  | 1.2 |  | 9 |  |  |  | 14
| T-45: Divided Power and Data with wire retainer & two divider walls (3 channels) (POWER) |  | 0.44 |  | NA |  |  |  | NA
| T-45: Divided Power and Data with wire retainer & two divider walls (3 channels) (DATA 1) |  | 0.68 |  | 5 |  |  |  | 8
| T-45: Divided Power and Data with wire retainer & two divider walls (3 channels) (DATA 2) |  | 0.44 |  | 3 |  |  |  | 5
| T-45: Divided Power and Data using the Offset Box (POWER) |  | 0.41 |  | NA |  |  |  | NA
| T-45: Divided Power and Data using the Offset Box (DATA) |  | 1.06 |  | 8 |  |  |  | 12
| T-45: Data only using data bracket |  | 2 |  | 16 |  |  |  | 24
| T-45 Divided Power and Data using Hinged Data Bracket with Divider Insert (POWER) |  | 0.52 |  | NA |  |  |  | NA
| T-45 Divided Power and Data using Hinged Data Bracket with Divider Insert (DATA) |  | 1.2 |  | 9 |  |  |  | 14
| T-45: Divided Power and Data using Electrical Bracket and Box (POWER) |  | 0.22 |  | NA |  |  |  | NA
| T-45: Divided Power and Data using Electrical Bracket and Box (DATA) |  | 0.5 |  | 4 |  |  |  | 6
LD Profile Raceway | LD3 |  | 0.21 |  | 1 |  |  |  | 2
| LD5 |  | 0.38 |  | 3 |  |  |  | 4
| LD10 |  | 1 |  | 8 |  |  |  | 12
| LDPH3 |  | 0.17 |  | 1 |  |  |  | 2
| LDPH5 |  | 0.33 |  | 2 |  |  |  | 4
| LDPH10 |  | 0.89 |  | 7 |  |  |  | 10
| LD2P10 - Left Channel |  | 0.43 |  | NA |  |  |  | NA
| LD2P10 - Right Channel |  | 0.5 |  | 4 |  |  |  | 6
| LDS3 |  | 0.21 |  | 1 |  |  |  | 2
| LDS5 |  | 0.38 |  | 3 |  |  |  | 4
Cove Raceway | WCM35: No devices |  | 5.4 |  | 44 |  |  |  | 66
| WCM35: Using Wire Retainer - no devices |  | 5 |  | 40 |  |  |  | 61
| WCM35: Divided Power and Data using Wire Retainer and Divider Wall (POWER) |  | 2.4 |  | NA |  |  |  | NA
| WCM35: Divided Power and Data using Wire Retainer and Divider Wall (DATA) |  | 2.4 |  | 19 |  |  |  | 29
| WCM35: Divided Power and Data using Device Box and Faceplate Adapter (POWER) |  | 1.4 |  | NA |  |  |  | NA
| WCM35: Divided Power and Data using Device Box and Faceplate Adapter (DATA) |  | 1.6 |  | 13 |  |  |  | 19
| WCM35: Divided Power and Data using Low Profile Transition Insert (POWER) |  | 1.8 |  | NA |  |  |  | NA
| WCM35: Divided Power and Data using Low Profile Transition Insert (DATA) |  | 2.4 |  | 19 |  |  |  | 29
Office Furniture Raceway | OFR20 |  | 2.3 |  | 18 |  |  |  | 28
Pan-Pole Aluminum Pole | Divided Power and Data: Snap-on Faceplates (POWER) |  | 0.47 |  | NA |  |  |  | NA
| Divided Power & Data: Snap-on Faceplates (DATA) |  | 2.75 |  | 22 |  |  |  | 33
| Divided Power & Data: Screw-on Faceplates (POWER) |  | 0.43 |  | NA |  |  |  | NA
| Divided Power and DATA: Screw-on Faceplates (DATA) |  | 2.15 |  | 17 |  |  |  | 26
| Communication Only: Snap- on Faceplates |  | 3.47 |  | 28 |  |  |  | 42
| Communication Only: Screw- on Faceplates |  | 2.83 |  | 23 |  |  |  | 34
Raceway Cable Fill Calculator V2

## numbers (hidden)
in. | no | 14
mm | yes | 12
10
40% | 40%
60% | 40%
0.215 | 0.185 | 0.275 | 0.15 | 0.235
NOTES: MAX FILL FOR POWER CABLES TAKEN FROM PREVIOUS CABLE FILL CHART